## Sheet1
Tiny_Reg | Tiny_Name | Tiny_Type | Tiny_Scale_Unit | Victron_CAN_ID | Victron_Field | Victron_Type_Unit | Offset | Bits | Direction | Mapping_Type | Compute_Inputs | Scale_Tiny_To_CAN | Formula | CAN_Priority | Comment
- | Charge Voltage Limit (CVL) | - | - | 0x351 | ChargeVoltageLimit | un16/0.1V | 0 | - | TX | Compute | fullyChargedVoltage,maxCellVoltage,bmsTemp,minChargeVoltage | - | CVL = max(minChargeVoltage, fullyChargedVoltage - fV(maxCellVoltage) - fT(bmsTemp)) | 1 | Dynamic CVL per code (reduce via cell V & temp)
103 | Max Charge Current | UINT16 | 0.1 A | 0x351 | MaxChargeCurrent CCL | sn16/0.1A | 2 | - | TX | Compute | maxChargeCurrent,bmsTemp,soc | ×1→(0.1A) | CCL = min(maxChargeCurrent, tempDerate, socDerate) | 1 | Positive value expected by Victron
102 | Max Discharge Current | UINT16 | 0.1 A | 0x351 | MaxDischargeCurrent DCL | sn16/0.1A | 4 | - | TX | Compute | maxDischargeCurrent,bmsTemp,soc | ×1→(0.1A) | DCL = min(maxDischargeCurrent, tempDerate, socDerate) | 1 | Positive value expected by Victron
46 | State Of Charge | UINT32 | 0.002 % | 0x355 | SOC | un16/% | 0 | - | TX | Direct | - | ×0.002→% (round) | SOC from Tiny high-res | 2 | Also fill hi-res if used
45 | State Of Health | UINT16 | 0.002 % | 0x355 | SOH | un16/% | 2 | - | TX | Direct | - | ×0.002→% (round) | SOH from Tiny | 2 | —
36 | Battery Pack Voltage | FLOAT | 1 V | 0x356 | BatteryVoltage | sn16/0.01V | 0 | - | TX | Direct | - | ×100 | Quantize to 0.01 V | 2 | —
38 | Battery Pack Current | FLOAT | 0,1 A | 0x356 | BatteryCurrent | sn16/0.1A | 2 | - | TX | Direct | - | ×10 | Sign: charge + / discharge – | 2 | —
48 | Internal Temperature | INT16 | 0.1 °C | 0x356 | BatteryTemperature | sn16/0.1°C | 4 | - | TX | Direct | - | ×1→(0.1°C) | — | 2 | —
36.315 | Battery High Voltage Alarm | UINT8 | - | 0x35A | BatteryHighVoltageAlarm | bits2 | 0 | 2 | TX | Compute | packVoltage,highVoltageCutoff | - | if packVoltage > highVoltageCutoff then 1 else 0 | 3 | Alarm (hard threshold)
36.316 | Battery Low Voltage Alarm | UINT8 | - | 0x35A | BatteryLowVoltageAlarm | bits2 | 0 | 4 | TX | Compute | packVoltage,lowVoltageCutoff | - | if packVoltage < lowVoltageCutoff then 1 else 0 | 3 | Alarm (hard threshold)
113.318 | Battery High Temperature Alarm | UINT8 | - | 0x35A | BatteryHighTempAlarm | bits2 | 0 | 6 | TX | Compute | maxTemp,highTempCutoff | - | if maxTemp > highTempCutoff then 1 else 0 | 3 | Alarm from Tiny temperature set
113.319 | Battery Low Temperature Alarm | UINT8 | - | 0x35A | BatteryLowTempAlarm | bits2 | 1 | 0-1 | TX | Compute | minTemp,lowTempCutoff | - | if minTemp < lowTempCutoff then 1 else 0 | 3 | Alarm from Tiny temperature set
42.319 | Battery High Temp Charge Alarm | UINT8 | - | 0x35A | BatteryHighTempChargeAlarm | bits2 | 1 | 2 | TX | Compute | externalTemp,highTempChargeCutoff | - | if externalTemp > highTempChargeCutoff then 1 else 0 | 3 | Charge temp alarm
42.32 | Battery Low Temp Charge Warning | UINT8 | - | 0x35A | BatteryLowTempChargeWarning | bits2 | 5 | 4 | TX | Compute | externalTemp,lowTempChargeCutoff | - | if externalTemp < lowTempChargeCutoff then 1 else 0 | 4 | Charge temp warning
38.317 | Battery High Current Alarm | UINT8 | - | 0x35A | BatteryHighCurrentAlarm | bits2 | 1 | 6 | TX | Compute | packCurrent,overCurrentCutoff | - | if packCurrent > overCurrentCutoff then 1 else 0 | 3 | Over-current alarm
38.318 | Battery High Charge Current Alarm | UINT8 | - | 0x35A | BatteryHighChargeCurrentAlarm | bits2 | 2 | 0-1 | TX | Compute | packCurrent,overChargeCurrentCutoff | - | if packCurrent > overChargeCurrentCutoff then 1 else 0 | 3 | Charge over-current alarm
52 | Cell Imbalance Alarm | UINT8 | - | 0x35A | CellImbalanceAlarm | bits2 | 3 | 0-1 | TX | Compute | balancingState | - | if balancingState != 0 then 1 else 0 | 4 | Imbalance present
36.315 | Battery High Voltage Warning | UINT8 | - | 0x35A | BatteryHighVoltageWarning | bits2 | 4 | 2 | TX | Compute | packVoltage,highVoltageCutoff | - | if packVoltage > (highVoltageCutoff*0.8) then 1 else 0 | 4 | Early warning @80%
36.316 | Battery Low Voltage Warning | UINT8 | - | 0x35A | BatteryLowVoltageWarning | bits2 | 4 | 4 | TX | Compute | packVoltage,lowVoltageCutoff | - | if packVoltage < (lowVoltageCutoff*1.2) then 1 else 0 | 4 | Early warning @120%
113.318 | Battery High Temperature Warning | UINT8 | - | 0x35A | BatteryHighTempWarning | bits2 | 4 | 6 | TX | Compute | maxTemp,highTempCutoff | - | if maxTemp > (highTempCutoff*0.8) then 1 else 0 | 4 | Early warning @80%
113.319 | Battery Low Temperature Warning | UINT8 | - | 0x35A | BatteryLowTempWarning | bits2 | 5 | 0-1 | TX | Compute | minTemp,lowTempCutoff | - | if minTemp < (lowTempCutoff*1.2) then 1 else 0 | 4 | Early warning @120%
42.319 | Battery High Temp Charge Warning | UINT8 | - | 0x35A | BatteryHighTempChargeWarning | bits2 | 5 | 2 | TX | Compute | externalTemp,highTempChargeCutoff | - | if externalTemp > (highTempChargeCutoff*0.8) then 1 else 0 | 4 | Charge warning @80%
42.32 | Battery Low Temp Charge Warning | UINT8 | - | 0x35A | BatteryLowTempChargeWarning | bits2 | 5 | 4 | TX | Compute | externalTemp,lowTempChargeCutoff | - | if externalTemp < (lowTempChargeCutoff*1.2) then 1 else 0 | 4 | Charge warning @120%
38.317 | Battery High Current Warning | UINT8 | - | 0x35A | BatteryHighCurrentWarning | bits2 | 5 | 6 | TX | Compute | packCurrent,overCurrentCutoff | - | if packCurrent > (overCurrentCutoff*0.8) then 1 else 0 | 4 | Current warning @80%
38.318 | Battery High Charge Current Warning | UINT8 | - | 0x35A | BatteryHighChargeCurrentWarning | bits2 | 6 | 0-1 | TX | Compute | packCurrent,overChargeCurrentCutoff | - | if packCurrent > (overChargeCurrentCutoff*0.8) then 1 else 0 | 4 | Charge current warning @80%
50 | BMS Internal Warning | UINT16 | - | 0x35A | BMSInternalWarning | bits2 | 6 | 6 | TX | Compute | systemStatusCode | - | if systemStatusCode == 0x9B then 1 else 0 | 4 | As per your table
51 | Need Balancing | UINT16 | - | 0x35A | CellImbalanceWarning | bits2 | 7 | 0-1 | TX | Compute | balancingDecision | - | if balancingDecision != 0 then 1 else 0 | 4 | Needs balancing
50 | System Status (online/offline) | UINT16 | - | 0x35A | SystemStatus | bits2 | 7 | 2 | TX | Compute | systemStatusCode | - | if systemStatusCode != 0x9B then 1 else 0 | 3 | Online if code != 0x9B
500 | Manufacturer Name | STRING(8) | ASCII | 0x35E | ManufacturerName | ASCII | 0 | - | TX | Direct | - | - | Constant (8 chars, pad with 0) | 5 | E.g., "TinyBMS" or project name
501.502 | Firmware Version | UINT16 | - | 0x35F | FirmwareVersion | un16 | 0 | - | TX | Direct | firmwareMajor,firmwareMinor | - | firmware = (major<<8)¦minor | 5 | Per your code
306 | Online Capacity | UINT16 | 0.01 Ah | 0x371 | OnlineCapacity | un16/Ah | 0 | - | TX | Direct | reg306 | - | onlineCapacity = reg306*100 | 5 | Keep if you really use 0x371 this way
- | Energy In | — | — | 0x378 | EnergyIn | un32/100Wh | 0 | - | TX | Compute | packVoltage,packCurrent,Δt | - | E_in += max(packCurrent,0)*packVoltage*Δt/3600 | 5 | Cumulative energy in
- | Energy Out | — | — | 0x378 | EnergyOut | un32/100Wh | 4 | - | TX | Compute | packVoltage,packCurrent,Δt | - | E_out += max(-packCurrent,0)*packVoltage*Δt/3600 | 5 | Cumulative energy out
- | Installed Capacity | UINT16 | Ah | 0x379 | InstalledCapacity | un16/Ah | 0 | - | TX | Compute | nominalCapacity,stateOfHealth | - | installedCapacity = nominalCapacity * SOH / 100 | 5 | Installed capacity (nominal × SOH)
502 | Battery Family | STRING(8) | ASCII | 0x382 | BatteryFamily | ASCII | 0 | - | TX | Direct | - | - | Constant family (8 chars) | 5 | e.g., "LiFePO4"
40 | Min Cell Voltage | UINT16 | 1 mV | — | — | — | — | — | — | InputOnly | minCellVoltage | - | — | — | Use if you add CAN 0x373 (recommended)
41 | Max Cell Voltage | UINT16 | 1 mV | — | — | — | — | — | — | InputOnly | maxCellVoltage | - | — | — | Use if you add CAN 0x373 (recommended)
42 | External Temperature #1 | INT16 | 0.1 °C | — | — | — | — | — | — | InputOnly | externalTemp | - | — | — | Optional for 0x373 min/max temperatures
305 | CAN Keep-Alive (Inverter→BMS) | — | — | 0x305 | KeepAlive | — | — | — | RX | InputOnly | — | — | — | — | Present in Victron spec (RX)
307 | Identification handshake (Inv→BMS) | — | — | 0x307 | Handshake | — | — | — | RX | InputOnly | — | — | — | — | Present in Victron spec (RX)
R/W | Description | Tiny_Type | Value
300 | Fully Charged Voltage [1200 to 4500] | [UINT_16] | 3650
301 | Fully Discharged Voltage [1000 to 3500] | [UINT_16] | 3250
303 | Early Balancing Threshold [1000 to 4500] | [UINT_16] | 3400
304 | Charge Finished Current [100 to 5000] | [UINT_16] | 1000
305 | Peak Discharge Current Cutoff | [UINT_16] | 70
306 | Battery Capacity [10 to 65500] | [UINT_16] | 314
307 | Number Of Series Cells [4 to 16] | [UINT_16] | 16
308 | Allowed Disbalance [15 to 100] | [UINT_16] | 15
310 | Charger Startup Delay [5 to 60] | [UINT_16] | 20
311 | Charger Disable Delay [0 to 60] | [UINT_16] | 5
315 | Over-Voltage Cutoff [1200 to 4500] | [UINT_16] | 3800
316 | Under-Voltage Cutoff [800 to 3500] | [UINT_16] | 2800
317 | Discharge Over-Current Cutoff [1 to 750] | [UINT_16] | 65
318 | Charge Over-Current Cutoff [1 to 750] | [UINT_16] | 90
319 | Over-Heat Cutoff [+20 to +90] | [UINT_16] | 60
320 | Low Temperature Charger Cutoff [-40 to +10] | [UINT_16] | 0
321 | Charge Restart Level [60-95] | [UINT_16] | 80
322 | Battery Maximum Cycles Count [10-65000] | [UINT_16] | 5000
323 | State Of Health [0 to 50000] | [UINT_16] | 100 | [0xFFFF – when data internally accepted]
328 | State Of Charge [0 to 50000] | [UINT_16] | 40
329 | Invert External Current Sensor Direction [1st bit] (0-1) |  | To be defined | Disable Load
330 | Charger Type [8 bits LSB] | [8 bits LSB] | 0x01 | 0x00-Variable (Reserved), 0x01-CC
331 | Load Switch Type [8 bits LSB] | [8 bits LSB] | To be defined | 0x00-FET, 0x01-AIDO1, 0x02-AIDO2, 0x03-DIDO1, 0x04-DIDO2, 0x05-AIHO1 Active Low, 0x06-AIHO1 Active High, 0x07-AIHO2 Active Low, 0x08-AIHO2 Active High
332 | Automatic Recovery [8 bits LSB] [1 to 30] | [8 bits LSB] | 5
333 | Charger Switch Type [8 bits LSB] | [8 bits LSB] | 0x01 | 0x01-Charge FET, 0x02-AIDO1, 0x03-AIDO2, 0x04-DIDO1, 0x05-DIDO2, 0x06-AIHO1 Active Low, 0x07-AIHO1 Active High, 0x08-AIHO2 Active Low, 0x09-AIHO2 Active High
334 | Ignition [8 bits LSB] | [8 bits LSB] | To be defined | 0x00-Disabled, 0x01-AID01, 0x02-AIDO2, 0x03-DIDO1, 0x04-DIDO2, 0x05-AIHO1, 0x06-AIHO2
335 | Charger Detection [8 bits LSB] | [8 bits LSB] | 0x01-Internal | 0x01-Internal, 0x02-AIDO1, 0x03-AIDO2, 0x04-DIDO1, 0x05-DIDO2, 0x06-AIHO1, 0x07-AIHO2
337 | Precharge Pin [8 bits LSB] | [8 bits LSB] | To be defined | 0x00-Disabled, 0x02-Discharge FET, 0x03-AIDO1, 0x04-AIDO2, 0x05-DIDO1, 0x06-DIDO2, 0x07-AIHO1 Active low, 0x08-AIHO1 Active high, 0x09-AIHO2 Active low, 0x10-AIHO2 Active high
338 | Precharge Duration [8 bits LSB] | [8 bits LSB] | 0x07 | 0x00-0.1 sec., 0x01-0.2 sec., 0x02-0.5 sec., 0x03-1 sec., 0x04-2 sec., 0x05-3 sec., 0x06-4 sec., 0x07-5 sec.
339 | Temperature Sensor Type [8 bits LSB] | [8 bits LSB] | 0x00 | 0x00-Dual 10K NTC, 0x01-Multipoint Active Sensor
340 | BMS Operation Mode [8 bits LSB] | [8 bits LSB] | 0x00 | 0x00-Dual Port Operation, 0x01-Single Port Operation
341 | Single Port Switch Type [8 bits LSB] | [8 bits LSB] |  | 0x00-FET, 0x01-AIDO1, 0x02-AIDO2, 0x03-DIDO1, 0x04-DIDO2, 0x05-AIHO1 Active Low, 0x06-AIHO1 Active High, 0x07-AIHO2 Active Low, 0x08-AIHO2 Active High
342 | Broadcast Time [8 bits LSB] | [8 bits LSB] | 0x00 | 0x00-Disabled, 0x01-0.1 sec., 0x02-0.2 sec., 0x03-0.5 sec., 0x04-1 sec., 0x05-2 sec., 0x06-5 sec., 0x07-10 sec.
343 | Protocol [8 bits LSB] | [8 bits LSB] | 0x01 | ASCII

## Feuil1
REG |  | std::vector<TinyRegisterRuntimeBinding> g_bindings = {
32 |  | {32, 1, 32, TinyRegisterValueType::Uint16, false, 1.0f, TinyLiveDataField::None, "Lifetime Counter", "-", nullptr},
36 |  | {36, 1, 36, TinyRegisterValueType::Float, false, 0.01f, TinyLiveDataField::Voltage, "Battery Pack Voltage", "V", nullptr},
38 |  | {38, 1, 38, TinyRegisterValueType::Float, true, 0.1f, TinyLiveDataField::Current, "Battery Pack Current", "A", nullptr},
40 |  | {40, 1, 40, TinyRegisterValueType::Uint16, false, 1.0f, TinyLiveDataField::MinCellMv, "Min Cell Voltage", "mV", nullptr},
41 |  | {41, 1, 41, TinyRegisterValueType::Uint16, false, 1.0f, TinyLiveDataField::MaxCellMv, "Max Cell Voltage", "mV", nullptr},
42 |  | {42, 1, 42, TinyRegisterValueType::Int16, true, 0.1f, TinyLiveDataField::None, "External Temperature #1", "°C", nullptr},
{43, 1, 43, TinyRegisterValueType::Int16, true, 0.1f, TinyLiveDataField::None, "External Temperature #2", "°C", nullptr},
45 |  | {45, 1, 45, TinyRegisterValueType::Uint16, false, 0.1f, TinyLiveDataField::SohPercent, "State Of Health", "%", nullptr},
46 |  | {46, 1, 46, TinyRegisterValueType::Uint16, false, 0.1f, TinyLiveDataField::SocPercent, "State Of Charge", "%", nullptr},
48 |  | {48, 1, 48, TinyRegisterValueType::Int16, true, 0.1f, TinyLiveDataField::Temperature, "Internal Temperature", "°C", nullptr},
50 |  | {50, 1, 50, TinyRegisterValueType::Uint16, false, 1.0f, TinyLiveDataField::OnlineStatus, "System Status", "-", nullptr},
51 |  | {51, 1, 51, TinyRegisterValueType::Uint16, false, 1.0f, TinyLiveDataField::BalancingBits, "Need Balancing", "-", nullptr},
52 |  | {52, 1, 52, TinyRegisterValueType::Uint8, false, 1.0f, TinyLiveDataField::None, "Cell Imbalance Alarm", "-", nullptr},
102 |  | {102, 1, 102, TinyRegisterValueType::Uint16, false, 0.1f, TinyLiveDataField::MaxDischargeCurrent, "Max Discharge Current", "A", nullptr},
103 |  | {103, 1, 103, TinyRegisterValueType::Uint16, false, 0.1f, TinyLiveDataField::MaxChargeCurrent, "Max Charge Current", "A", nullptr},
113 |  | MinPackTemp, MaxPacktemp
{305, 1, 305, TinyRegisterValueType::Uint16, false, 1.0f, TinyLiveDataField::None, "Victron Keep-Alive", "-", nullptr},
306 |  | {306, 1, 306, TinyRegisterValueType::Uint16, false, 0.01f, TinyLiveDataField::None, "Battery Capacity", "Ah", nullptr},
{307, 1, 307, TinyRegisterValueType::Uint16, false, 1.0f, TinyLiveDataField::None, "Identification Handshake", "-", nullptr},
315 |  | Overvoltage
316 |  | Undervoltage
317 |  | DischargeoverCurrent
318 |  | ChargeoverCurrent
319 |  | OverHeatcutof
500 |  | {500, 4, 500, TinyRegisterValueType::String, false, 1.0f, TinyLiveDataField::None, "Manufacturer Name", nullptr, nullptr},
501 |  | {501, 2, 501, TinyRegisterValueType::Uint32, false, 1.0f, TinyLiveDataField::None, "Firmware Version", nullptr, nullptr},
502 |  | {502, 4, 502, TinyRegisterValueType::String, false, 1.0f, TinyLiveDataField::None, "Battery Family", nullptr, nullptr}
113 | Battery High Temperature Alarm | UINT8 | - | 0x35A | BatteryHighTempAlarm | bits2 | 0 | 6 | TX | Compute | maxTemp,highTempCutoff | - | if maxTemp > highTempCutoff then 1 else 0 | 3 | Alarm from Tiny temperature set
113 | Battery Low Temperature Alarm | UINT8 | - | 0x35A | BatteryLowTempAlarm | bits2 | 1 | 0-1 | TX | Compute | minTemp,lowTempCutoff | - | if minTemp < lowTempCutoff then 1 else 0 | 3 | Alarm from Tiny temperature set
36.315 | Battery High Voltage Warning | UINT8 | - | 0x35A | BatteryHighVoltageWarning | bits2 | 4 | 2 | TX | Compute | packVoltage,highVoltageCutoff | - | if packVoltage > (highVoltageCutoff*0.8) then 1 else 0 | 4 | Early warning @80%
36.316 | Battery Low Voltage Warning | UINT8 | - | 0x35A | BatteryLowVoltageWarning | bits2 | 4 | 4 | TX | Compute | packVoltage,lowVoltageCutoff | - | if packVoltage < (lowVoltageCutoff*1.2) then 1 else 0 | 4 | Early warning @120%
38.317 | Battery High Current Warning | UINT8 | - | 0x35A | BatteryHighCurrentWarning | bits2 | 5 | 6 | TX | Compute | packCurrent,overCurrentCutoff | - | if packCurrent > (overCurrentCutoff*0.8) then 1 else 0 | 4 | Current warning @80%
113.318 | Battery High Temperature Warning | UINT8 | - | 0x35A | BatteryHighTempWarning | bits2 | 4 | 6 | TX | Compute | maxTemp,highTempCutoff | - | if maxTemp > (highTempCutoff*0.8) then 1 else 0 | 4 | Early warning @80%
113.319 | Battery Low Temperature Warning | UINT8 | - | 0x35A | BatteryLowTempWarning | bits2 | 5 | 0-1 | TX | Compute | minTemp,lowTempCutoff | - | if minTemp < (lowTempCutoff*1.2) then 1 else 0 | 4 | Early warning @120%
42.319 | Battery High Temp Charge Warning | UINT8 | - | 0x35A | BatteryHighTempChargeWarning | bits2 | 5 | 2 | TX | Compute | externalTemp,highTempChargeCutoff | - | if externalTemp > (highTempChargeCutoff*0.8) then 1 else 0 | 4 | Charge warning @80%